## Zonelark FCA Log
Fixed ID Number | Facility Name | Facility Type/Usage | Facility Level/Floor | Room Number | Room Name | Area / Asset Served | Asset / CMMS ID (e.g. TAG #) | Asset Name (e.g. AHU-3) | Asset Manufacturer | Asset Model Number | Asset Serial Number | Asset Approximate Install Year | Notes/Comments | FCA 1-5 | Asset Type | Asset "Size" | Asset Quantity Multiplier | Unit of Measure | Asset Repair or Replace | Uniformat Level 2 | Industry Life Expectancy | Industry Replacement Year | Industry Life Remaining | Estimated / Observed Life Remaining | Observed Replacement Year | Unit Probable Cost ($) (MANUAL ENTRY POSSIBLE) | Extended Probable Cost ($) | Depreciated Value | Annual Maintenance | Facility Square Feet | Date of Assessment | Operational Impact (1-5) | Energy Impact (1-5)
01 | Riverside Medical Center | Healthcare | Basement | B-101 | Mechanical Room | ICU Wing / OR Suite | AHU-001 | AHU-1 | Carrier | 39MBB030 | 2918KA07263 | 2008 | Minor corrosion on drain pan. Filter housing bent. | 3 | Air Handling Unit | 30 Ton | 1 | EA | Repair | D30 HVAC | 20 |  |  | 4 | 2030 | 18000 |  |  |  | 85000 | 2026-06-25 | 5 | 5
01 | Riverside Medical Center | Healthcare | Roof Level | R-01 | Rooftop Mechanical | Admin Wing | RTU-002 | RTU-2 | Lennox | LGH240H4BM1G | 5820H24568 | 2015 | Economizer damper seized. Refrigerant charge OK. | 2 | Packaged Rooftop Unit | 20 Ton | 1 | EA | Repair | D30 HVAC | 15 |  |  | 2 | 2028 | 22000 |  |  |  | 85000 | 2026-06-25 | 4 | 5
01 | Riverside Medical Center | Healthcare | Basement | B-102 | Boiler Room | Perimeter Radiation / Domestic HW | BLRP-001 | BLR-1 | Cleaver-Brooks | ClearFire-C CF-200 | CB-20213847 | 2012 | Annual service completed. Burner assembly cleaned. | 4 | Boiler | 200 BHP | 2 | EA | Maintain | D30 HVAC | 25 |  |  | 11 | 2037 | 48000 |  |  |  | 85000 | 2026-06-25 | 5 | 4
02 | Riverside Medical Center | Healthcare | 2nd Floor | E-201 | Electrical Room | Full Building | XFMR-001 | XFMR-1 | Square D | EX75T3HCU | 9827A44821 | 2005 | Discoloration on secondary terminals. NETA test recommended. | 2 | Dry Type Transformer | 75 kVA / 480-208Y/120V | 1 | EA | Replace | D50 Electrical | 35 |  |  | 1 | 2027 | 20000 |  |  |  | 85000 | 2026-06-25 | 5 | 1
02 | Riverside Medical Center | Healthcare | 2nd Floor | E-201 | Electrical Room | Critical Life Safety Circuit | GENSET-001 | GENSET-1 | Cummins | C500D6R | J-100012245 | 2018 | Load bank test 2025-11. Transfer time within spec. | 5 | Emergency Generator | 500 kW / 480V | 1 | EA | Maintain | D50 Electrical | 25 |  |  | 17 | 2043 | 60000 |  |  |  | 85000 | 2026-06-25 | 5 | 2
01 | Riverside Medical Center | Healthcare | Basement | B-105 | Domestic Water Room | Building-Wide DHW | WH-001 | WH-1 | A.O. Smith | BTXL-120-ASME | AOS-190874621 | 2017 | Sacrificial anode condition unknown. Schedule service. | 3 | Commercial Water Heater | 120 Gal / 300 MBH | 3 | EA | Maintain | D20 Plumbing | 15 |  |  | 6 | 2032 | 9500 |  |  |  | 85000 | 2026-06-25 | 4 | 2
01 | Riverside Medical Center | Healthcare | Basement | B-110 | Fire Pump Room | Sprinkler System – Full Building | FP-001 | FP-1 | Peerless | AE4AE-20 | PRL-20172271 | 2010 | Annual fire pump test passed. Packing gland drips slightly. | 4 | Fire Pump | 750 GPM @ 100 PSI | 1 | EA | Maintain | D40 Fire Protection | 20 |  |  | 4 | 2030 | 20000 |  |  |  | 85000 | 2026-06-25 | 5 | 1
01 | Riverside Medical Center | Healthcare | 1st Floor | 112 | Fire Command Center | Campus-Wide Life Safety | FACP-001 | FACP-1 | Notifier | NFS2-3030 | NTF-20091188 | 2009 | Firmware out of support. Six zone cards showing supervisory fault. | 2 | Fire Alarm Control Panel | 3030 Points | 1 | EA | Replace | D40 Fire Protection | 15 |  |  | 0 | 2026 | 14000 |  |  |  | 85000 | 2026-06-25 | 5 | 1
TOTALS / PORTFOLIO SUMMARY

## output-capX
Inflation Rate: | 5%
Facility Name | NPV (30 Yr) | Year. 1 | Year. 2 | Year. 3 | Year. 4 | Year. 5 | Year. 6 | Year. 7 | Year. 8 | Year. 9 | Year. 10 | Year. 11 | Year. 12 | Year. 13 | Year. 14 | Year. 15 | Year. 16 | Year. 17 | Year. 18 | Year. 19 | Year. 20 | Year. 21 | Year. 22 | Year. 23 | Year. 24 | Year. 25 | Year. 26 | Year. 27 | Year. 28 | Year. 29 | Year. 30
Riverside Medical Center
TOTAL — ALL FACILITIES